LATERAL LOAD PATH

QA/QC REVIEW REPORT

[Institutional Building Renovation — name and location redacted]

Project No. [redacted]

Bid Documents, dated [redacted] (Sheets S1.0, S1.1; the full 24-sheet bid set was reviewed for lateral and nonstructural items)

Prepared by: [Reviewer Name]

Date: [Report Date]

Scope: Lateral (Seismic) Load Path and Design Basis (V3)

This report traces the lateral load path and checks the stated seismic design basis and detailing qualitatively. It does not include load-magnitude or capacity calculations, and it does not replace the engineer of record's responsibility or plan check.

# Executive Summary

This report documents a lateral load path review of the structural sheets (S1.0, S1.1) in the bid set for an existing one-story, split-level institutional building with a crawl space. The full 24-sheet set was also reviewed for lateral and nonstructural items. The structural scope is a floor-leveling and floor-framing repair: new LVL members sistered to existing dropped beams, a rebuilt central beam line on new CMU piers, steel end brackets at the exterior brick walls, and floor sheathing replacement in two rooms. The structural general notes state the existing structure is not being brought up to current code for wind or seismic loads.

The existing lateral system appears to be perimeter brick bearing walls with wood floor and roof diaphragms. No as-built lateral information is in the set, so the typical lateral path (diaphragm, wall anchorage, walls, foundation) could not be confirmed at any link. That is expected for this scope and is recorded as informational. The review then traced the new work that touches the lateral path.

Seven findings result: one design-basis inconsistency (no seismic basis or SDC on the structural sheets, while the architectural notes require SDC D ceilings); three broken or unconfirmed path items (floor sheathing replacement without a nailing specification, no positive beam-to-support connection at the new piers, and nonstructural anchorage details); one detailing item to confirm (unreinforced new CMU piers if SDC D applies); one informational existing-condition note; and one reference gap for the skill itself (non-California code edition, IEBC alteration triggers, ceilings and lifts, and wind).

# Scope & Limitations

This review covers the lateral load path, the stated seismic design basis, and the detailing of new work, qualitatively. It does not cover:

- Load magnitude, member sizing, or capacity checks.

- The gravity load path. See the V2 gravity-load-path-qaqc example on the same set.

- Wind load determination. The wind basis is stated as "existing to remain" and was not reviewed.

- Roof framing. There is no roof framing plan in the set; the roof is identified as wood trusses only from the architectural partition detail.

- Existing-building evaluation (IEBC / ASCE 41). The documents state the structure is not being upgraded, and no as-built lateral information is provided.

Code basis: the set cites IBC 2021, which references ASCE 7-16. The skill's references are written to ASCE 7-22. Provisions cited in this report (for example §12.1.3 load path continuity and §12.1.4 connection to supports) are the same in both editions. Items that depend on IBC/IEBC, SDPWS, or TMS 402 are marked "verify" and are written as confirmation requests, not hard findings.

# System Identification & Design Basis

- Lateral system, both directions: presumed existing perimeter brick bearing walls (multi-wythe masonry hatch on S1.0/S1.1). No Table 12.2-1 system applies, because this is existing construction not being upgraded.

- Diaphragms: existing wood floor over the crawl space (joists on dropped beams and masonry piers); existing roof of wood trusses with unknown sheathing. Classification not stated.

- Irregularities: split-level building (T1.1 Code Note 3) implies a stepped diaphragm between the main block and the multipurpose wing. Plan shape includes re-entrant corners at the wing. Neither is evaluated in the documents.

- Foundation: existing exterior wall foundations (not shown); new 24"x24"x8" concrete pier bases on an assumed 1,500 psf soil value.

- Supported components: suspended ceilings (SDC D per architectural notes), braced wood partitions, a replacement enclosed vertical platform lift, and new windows in existing openings.

## Design Basis: Stated vs. Expected

| Item | Stated on Drawings | Expected | Status |
| --- | --- | --- | --- |
| Code edition | IBC 2021 (S1.0, General Note 2) | IBC 2021 references ASCE 7-16; existing-building work falls under the IEBC 2021 (verify: IEBC). The skill's ASCE 7-22 references were applied only where the provision is the same in ASCE 7-16. | Flag: IEBC compliance method not stated |
| Seismic / wind basis | "Snow, wind, seismic loads: existing building to remain. Structure not brought up to meet current codes." (S1.0, Note 1.C) | A statement of the existing-building compliance path showing the alterations do not trigger lateral upgrade (verify: IEBC 2021 alteration provisions) | Flag |
| Risk category / I_e | Not stated | Stated on general notes. Assembly area of 261 occupants (T1.1); confirm RC II vs. III per IBC Table 1604.5 | Flag |
| Site class; S_DS, S_D1 | Not stated | Stated, from the ASCE 7-16 values for the site | Flag |
| SDC | Not stated on structural sheets. Architectural T1.1 General Note 6: ceilings and ceiling-mounted fixtures "per current code as Seismic Design Category D" | One SDC, stated on the structural sheets and consistent with the architectural requirement | Flag: inconsistent / incomplete |
| SFRS (each direction) | Not stated | Existing: appears to be perimeter brick bearing walls with wood floor and roof diaphragms (not confirmed, no as-built information) | Informational |
| R / Ω₀ / C_d; ρ | Not stated | Not applicable unless the alteration triggers lateral evaluation | N/A |
| Diaphragm classification | Not stated | Existing wood floor and roof diaphragms; not applicable unless lateral evaluation is triggered | N/A |
| Analysis procedure, base shear, drift | Not stated | Not applicable unless lateral evaluation is triggered | N/A |
| Soil | Assumed allowable bearing 1,500 psf (S1.0 Soil Note 1); no geotechnical report | Adequate for the gravity sizing of new pier bases; no lateral soil values are needed for the new work | OK for scope |

# Load Path Trace

## Typical Line of Resistance: Exterior Brick Wall Line (N-S; E-W walls are the same type)

Representative condition: the long exterior brick wall line, which is the only apparent vertical lateral element in each direction. The end walls (E-W) are the same construction and would trace the same way. Every link below is existing construction with no information in the set.

| Link | Element | Mechanism / Force Direction | Verified? | Notes / Flags |
| --- | --- | --- | --- | --- |
| 1. Load into diaphragm | Floor and roof mass; exterior brick walls loaded out-of-plane | Wall-to-floor and wall-to-roof anchorage | Not shown (existing) | No wall anchorage, ledger, or wall-pocket detail in the set. Roof is wood trusses (A1.2 partition detail); no roof framing or sheathing information. |
| 2. Across diaphragm / chords | Existing wood floor sheathing on existing joists | Sheathing nailed to joists; chords at the perimeter rim or wall bearing | Not shown (existing) | Sheathing type and nailing unknown. Sheathing is being replaced in two rooms; see Atypical Condition A. |
| 3. Into vertical element | Floor diaphragm to exterior brick wall | Joist or rim bearing in the wall, or ledger (unknown) | Not shown (existing) | No detail at the floor-to-wall interface. |
| 4. Down the vertical element | Exterior brick walls (hatched multi-wythe masonry on S1.0/S1.1) | In-plane shear through the masonry (presumed unreinforced) | Not shown (existing) | Reinforcement, grout, and wythe ties unknown. Typical of an unreinforced masonry bearing-wall building of this type. |
| 5. Overturning path | Wall self-weight | No hold-downs (masonry wall) | Not shown (existing) | Consistent with presumed URM; no further information. |
| 6. Base anchorage | Brick wall to its foundation | Unknown | Not shown (existing) | No foundation wall or footing section for the exterior walls. |
| 7. Foundation / soil | Existing exterior wall footing | Bearing, friction | Not shown (existing) | No footing information; soil value given only for new pier bases. |

## Atypical Conditions: Individually Traced

These conditions differ from the typical line, or are new work that touches the lateral path, and were traced individually.

| Condition / Location | Path | Mechanism / Required Basis | Verified? | Notes / Flags |
| --- | --- | --- | --- | --- |
| A. Floor sheathing replacement — Nursing 101 and Classroom 102 (S1.1 plan notes; A1.1 keynote A1) | New sheathing panels in the floor diaphragm, adjacent to the exterior brick walls | Panel edge and boundary nailing, blocking, and connection to the existing sheathing and the wall-side boundary | No | S1.1 says "remove and replace floor sheathing" and A1.1 keynote A1 says "see structural", but neither gives sheathing, nailing, or blocking. These areas are part of the diaphragm path into the exterior walls. See Finding 2. |
| B. New corridor beam line — 5¼"x11¼" LVL on new 16"x16" grouted CMU piers on 24"x24" concrete bases; ends on steel bent-plate brackets at the exterior brick walls | Beam supported by piers; ends tied to the wall through brackets | Positive connection to supports for a horizontal force parallel to the member (5% of D+L reaction, ASCE 7-16/7-22 §12.1.4); lateral restraint at pier tops and bases | Partial | Piers: LVL is "placed tight to bottom of existing floor joists" and shimmed; no fastener between LVL and pier, and no dowel from pier to base. Ends: each bracket has (4) 3/4" epoxy bolts with 6" embed in existing brick and (4) 5/8" lag bolts into the LVL. This is a positive connection, but its design basis for horizontal force is not documented. See Findings 3 and 4. |
| C. New 16"x16" CMU piers (grout solid) | Isolated masonry pier between beam and base | Masonry column detailing for the SDC | Verify | No longitudinal reinforcement, ties, or dowels shown. If SDC D applies (per T1.1 Note 6), confirm the TMS 402 requirements for masonry columns (verify: TMS 402). See Finding 4. |
| D. Sistered existing dropped beams on retained piers (most bays) | Gravity reinforcement only | No change to the lateral path | Matches typical | The LVL sistering ((3) 10d or #12 screws at 12") doesn't create or remove a lateral link. The existing beam-to-pier connections stay as they are. |
| E. Split-level building (T1.1 Code Note 3); multipurpose wing at a different level | Stepped diaphragm between levels | A designed element transferring diaphragm force between levels | Not shown (existing) | The split level isn't in the structural scope. It's recorded because a stepped diaphragm is an atypical lateral condition (see the skill's diaphragms reference). |
| F. Nonstructural: suspended ceilings (SDC D per T1.1 Note 6), braced partitions (A1.2), replacement vertical platform lift (A1.1 keynote A2) | Components anchored to the structure | Component anchorage and bracing for F_p | Partial | A1.2 includes ASTM E580 ceiling guidance for SDC D-F. The partition "brace to structure above" detail has no fastener. Lift anchorage is by the manufacturer ("reuse existing infrastructure"). See Finding 5. |

# Findings

Ranked by effect on the lateral load path. "Verify" items are confirmation requests against the governing document.

| No. | Type | Location / Sheet | Finding | Code Reference | Recommended Action |
| --- | --- | --- | --- | --- | --- |
| 1 | Design-basis inconsistency | S1.0 General Note 1.C; T1.1 General Note 6 | The structural notes give no seismic basis (no RC, site class, S_DS/S_D1, or SDC) and state the existing structure is not brought up to current code, but don't state the existing-building compliance path. The architectural notes require ceilings to be installed for SDC D. | IBC 2021 §1603.1.5 (verify: IBC); IEBC 2021 alteration provisions (verify: IEBC) | Add the seismic design parameters and SDC to the structural general notes so the nonstructural requirements have a stated basis. State the IEBC compliance method, and confirm the alterations do not reduce the lateral capacity of the existing structure. |
| 2 | Broken / unconfirmed path | S1.1 — Nursing 101, Classroom 102; A1.1 keynote A1 | Floor sheathing is removed and replaced in two rooms that adjoin the exterior walls, but no sheathing thickness, grade, panel layout, edge/boundary/field nailing, or blocking is given. The new panels must restore the floor diaphragm's continuity into the walls. Each document defers to the other. | Load path continuity, ASCE 7-16 §12.1.3; SDPWS diaphragm construction (verify: SDPWS) | Provide a sheathing and nailing specification for the replacement areas that matches or exceeds the existing diaphragm, including edge blocking or support and the connection to adjacent existing sheathing and the wall boundary. (This is the same detail gap the V2 gravity review found for subfloor attachment.) |
| 3 | Broken / unconfirmed path | S1.1 — New LVL's and CMU Piers detail | No positive connection is shown between the new LVL beam and the new piers (shim only), or between the piers and their concrete bases. The end brackets are a positive connection, but their horizontal-force basis is not documented. | ASCE 7-16 §12.1.4 (same in 7-22): positive connection for 5% of D+L reaction parallel to the member | Confirm the end brackets are designed to provide the §12.1.4 connection for the continuous beam line, or add beam-to-pier connections (for example straps or clip angles). Show a pier-to-base dowel or keyed bearing if lateral restraint of the pier is relied on. |
| 4 | Detailing non-conformance (confirm) | S1.1 — 16"x16" CMU pier | The new isolated CMU piers are grouted but unreinforced, with no dowels to the base. If the project is SDC D (per T1.1), isolated masonry piers or columns typically need reinforcement and ties. | TMS 402 masonry column and seismic requirements (verify: TMS 402); ASCE 7-16 §14.4 | Confirm the classification and SDC requirements for the new piers. Add longitudinal reinforcement, ties, and base dowels if required, or document why plain masonry is permitted. |
| 5 | Broken / unconfirmed path (nonstructural) | A1.2 partition bracing detail; A1.1 keynote A2 (lift) | The partition top bracing detail says "brace to structure above" with no fastener or spacing. The replacement vertical platform lift reuses existing infrastructure, with no anchorage basis shown. | ASCE 7-16 Ch. 13 (component anchorage), if SDC D applies | Specify partition top bracing fasteners. Require the lift submittal to include seismic anchorage design for the stated SDC. |
| 6 | Informational (existing condition) | Building-wide | The existing building appears to be a masonry bearing-wall building with wood diaphragms, a type that is vulnerable to wall-to-diaphragm anchorage failure. No as-built lateral information is in the set, and the notes state the structure is not being upgraded. | IEBC 2021 / ASCE 41 (verify) | No action required for this permit unless IEBC triggers apply. Recommend the owner be informed of the building type for future planning. |
| 7 | Reference gap | Skill references | (a) The project is outside California and uses IBC 2021 / ASCE 7-16; the skill's references are written to ASCE 7-22. (b) IEBC alteration triggers for lateral systems are not covered. (c) Ceiling (ASTM E580) and lift anchorage are not covered in the nonstructural reference. (d) The wind basis is not covered. | — | Expand the skill references (see the test notes accompanying this example). |

# Appendix

## Details and Schedules Relied On

- S1.0 General Notes 1-8, Soil Notes 1-2, and Existing and Demolition Plan.

- S1.1 Framing Plan; details: New LVL's to Existing Dropped Beams; New LVL's and CMU Piers; Typical LVL Splice Detail; Wood Beam Bracket Detail; Beam Bearing Detail with Bracket.

- T1.1 Code Review Notes (split level; occupancy) and General Note 6 (SDC D ceilings).

- A1.1 keynotes A1 (new subfloor) and A2 (vertical platform lift); A1.2 partition bracing detail and ceiling seismic guidance.

- No typical/standard structural detail was relied on in place of a project-specific one. The wall anchorage, floor-to-wall connection, and exterior wall foundation are simply not shown.

## Items to Confirm Against Governing Documents

- IEBC 2021: alteration level and any lateral-evaluation trigger for this scope (for example, alterations that reduce lateral capacity or increase demand).

- IBC 2021 §1603.1.5: earthquake design data required on the construction documents for alterations.

- SDPWS: sheathing and nailing for the replacement diaphragm areas.

- TMS 402: reinforcement requirements for isolated masonry piers or columns in the governing SDC.

- ASCE 7-16 Chapter 13: ceiling and lift requirements, if SDC D applies.